## Constant Reactive Power
Test Steps
Set EUT to V_nom | 277 |  |  | Maximum Voltage AC | 318.55 | V | L-N
Set EUT to Nominal Frequency | 60 |  |  | Nominal Voltage AC | 277 | V
Set DC to nominal | 900 |  |  | Minimum Voltage AC | 243.76 | V
Set EUT to Prated | 63000 |  |  | a_v | 4.155 | V
Enable Constant Reactive Power Mode
Set to Q_max inj | 63000 |  |  | Maximum Voltage DC | 870 | Vdc
Set EUT to 20% of Prated | 12600 |  |  | Nominal Voltage DC | 900 | Vdc
Set EUT to 5% of Prated | 3150 |  |  | Minimum Voltage DC | 1247 | Vdc
Set EUT to Prated | 63000
Step AC to V_L + a_v | 247.915 |  |  | Minimum Power | 12600 | W
Step AC to V_H - a_v | 314.395 |  |  | Prated | 63000 | W
Step AC to V_L + a_v | 247.915
Step AC to V_N | 277 |  |  | Nominal Frequency | 60 | Hz
Step Phase A to 1.07V_N and Phase B and C to 0.91V_N | 296.39 | 252.07 | 252.07
Step AC to V_N | 277 |  |  | Q_max inj | 63000 | Var
Step Phase A to 0.91V_N and Phase B and C to 1.07V_N | 252.07 | 296.39 | 296.39 | Q_max abs | -63000 | Var
Step AC to V_N | 277
Turn off Reactive Power Mode
Repeat rows 2 - 19 for Q_max abs, 0.5 Q_max inj, 0.5 Q_max abs
Repeat rows 2-21 for Max Vdc and Min Vdc

## Watt-Var
Test Steps | Category 1 |  | Category 2 |  | Category 3
Connect the EUT according to the manufacturer specifications | [7 empty] | Maximum Voltage AC | 318.55 | V | L-N
Set EUT to nominal voltage | [7 empty] | Nominal Voltage AC | 277 | V
Set EUT to nominal frequency
Set EUT to rated active power condition | [7 empty] | Minimum Voltage AC | 243.76 | V
Set all voltage trip parameters to the default settings | [7 empty] | a_v | 4.155 | V
Set Watt-Var characteristics according to the respective characteristic. All other functions should be truned off.
Recode Applicable settings | [7 empty] | Maximum Voltage DC | 870 | Vdc
[8 empty] | Nominal Voltage DC | 900 | Vdc
[8 empty] | Minimum Voltage DC | 1247 | Vdc
[8 empty] | Minimum Power | 12600 | W
[8 empty] | Prated | 63000 | W
[8 empty] | Nominal Frequency | 60 | Hz
[8 empty] | Q_max inj | 63000 | Var
[8 empty] | Q_max abs | -63000 | Var
Repeat rows 2 - 17 for 20% and 60% power | [7 empty] | 0.2 Prated | 12600
Repeat rows 2 - 19 for characteristic 2 and 3
| Characteristic 1 |  |  | Characteristic 2 |  | Characteristic 3
P1 | 0.2 Prated or Pmin, greater of the two | 12600 |  | 0.2 Prated or Pmin, greater of the two | 12600 | 0.2 Prated or Pmin, greater of the two | 12600
P2 | 0.5 Prated | 31500 |  | 0.5 Prated | 31500 | 0.5 Prated | 31500
P3 | Prated | 63000 |  | Prated | 63000 | Prated | 63000
P'1 | 0.2 P'rated or P'min, lesser of the two | 12600 |  | 0.2 P'rated or P'min, lesser of the two | 12600 | 0.2 P'rated or P'min, lesser of the two | 12600
P'2 | 0.5 P'rated | 31500 |  | 0.5 P'rated | 31500 | 0.5 P'rated | 31500
P'3 | P'rated | 63000 |  | P'rated | 63000 | P'rated | 63000
Q1 | 0 | 0 |  | 22% of apparent nameplate rating, abs | -13860 | 0 | 0
Q2 | 0 | 0 |  | 22% of apparent nameplate rating, abs | -13860 | 44% of apparent nameplate rating, abs | -27720
Q3 | 44% of apparent nameplate rating, abs | -27720 |  | 44% of apparent nameplate rating, abs | -27720 | 44% of apparent nameplate rating, abs | -27720
Q'1 | 0 | 0 |  | 22% of apparent nameplate rating, inj | 13860 | 0 | 0
Q'2 | 0 | 0 |  | 22% of apparent nameplate rating, inj | 13860 | 44% of apparent nameplate rating, inj | 27720
Q'3 | 44% of apparent nameplate rating, inj | 27720 |  | 44% of apparent nameplate rating, inj | 27720 | 44% of apparent nameplate rating, inj | 27720

## Volt - Watt
Test Steps | Category 1 |  | Category 2 |  | Category 3
Set voltage to Nominal Voltage | 277 |  | 277 |  | 277 |  |  | Maximum Voltage AC | 318.55 | V | L-N
Set frequency to nominal | 60 |  | 60 |  | 60 |  |  | Nominal Voltage AC | 277 | V
Verify Volt Watt Mode is on | [7 empty] | Minimum Voltage AC | 243.76 | V
Step AC to V_L + a_v | 247.915 |  | 247.915 |  | 247.915 |  |  | a_v | 4.155 | V
Step AC to V_1 - a_v | 289.465 |  | 286.695 |  | 297.775
Step AC to V_1 + a_v | 297.775 |  | 295.005 |  | 306.085 |  |  | Maximum Voltage DC | 870 | Vdc
Step AC to (V_1+V_2)/2 | 299.16 |  | 297.775 |  | 303.315 |  |  | Nominal Voltage DC | 900 | Vdc
Step AC to V_2 - a_v | 300.545 |  | 300.545 |  | 300.545 |  |  | Minimum Voltage DC | 1247 | Vdc
Step AC to V_2 + a_v | 308.855 |  | 308.855 |  | 308.855
Step AC to V_H - a_v | 314.395 |  | 314.395 |  | 314.395 |  |  | Minimum Power | 12600 | W
Step AC to V_2 + a_v | 308.855 |  | 308.855 |  | 308.855 |  |  | Prated | 63000 | W
Step AC to V_2 - a_v | 300.545 |  | 300.545 |  | 300.545
Step AC to (V_1+V_2)/2 | 299.16 |  | 297.775 |  | 303.315 |  |  | Nominal Frequency | 60 | Hz
Step AC to V_1 - a_v | 289.465 |  | 286.695 |  | 297.775
Step AC to V_1 + a_v | 297.775 |  | 295.005 |  | 306.085 |  |  | Q_max inj | 63000 | Var
Step AC to V_L + a_v | 247.915 |  | 247.915 |  | 247.915 |  |  | Q_max abs | -63000 | Var
Repeat rows 2 - 17 for 20% and 60% power
Repeat rows 2 - 19 for characteristic 2 and 3
| Category 1 |  |  | Category 2 |  | Category 3
V_1 | 1.06 V_N | 293.62 |  | 1.05 V_N | 290.85 | 1.09 V_N | 301.93
P_1 | Prated | 63000 |  | Prated | 63000 | Prated | 63000
V_2 | 1.1 V_N | 304.7 |  | 1.1 V_N | 304.7 | 1.1 V_N | 304.7
P_2 | 0.2 Prated | 12600 |  | 0.2 Prated | 12600 | 0.2 Prated | 12600
P'2 | 0 |  |  | P'rated | 63000 | P'rated | 63000
ORLT | 10s |  |  | 90s |  | 0.5s